## Version History (hidden)
Amendment Record
Version | Date | Author | Amendment Overview
1 | 2019-12-18 | Kaisui Tnay | Original
1.1 | 2020-02-07 | Lindsay Speyers | Addition of Sanction to Connect form: - Addition of Remote Monitoring Tests tab - Addition of Anti-Islanding Tests tab - Addition of Submission Documents tab - Update to Site Details tab - Small changes to formatting in the inverter details tab

## Readme
This is a reference example only, ensure details are filled out according to YOUR specific system settings.
The example shown is based off a site with the following equipment: | 1. Site Details | 2. Inverter Details |  | 3. Inverter Prot and Control
4. DC Connections |  | 5. Anti-Islanding Tests | 6. Remote Monitoring Tests
7. Submission Checklist
UE EG Comissioning Form
This form replaces the previous Sanction to Connect form and the AEMO required DERR (Distributed Energy Resources Register) form.
The DERR form was a new requiremnt of AEMO for all new embedded generation applications as of 1 December 2019.
Below is outline for filling out this form. Refer to the sample example of each sheet (to the right>>) for more information on the required format.
1. Fill out each of the seven tabs at the bottom of the spreadsheet fully. Please only fill in the blue coloured boxes.
2. For additional information on data to be entered into a cell, hover curser over small red triangle.

## Site Details
Installation Site Details
UE Project Reference Number:
NMI:
Unit/House Number:
Street Address:
Suburb:
Postcode:
End Customer (Generator Owner)
Company Name:
Contact Person:
Position within Organisation:
Contact Number:
Email Address:
Site Operational Contact | Leave blank if same as above
Company Name:
Contact Person:
Position within Organisation:
Contact Number:
Email Address:
Installer Details
Company Name
Contact Name:
REC Number:
CEC Accreditation Number:
Installer Email:
Installer Mobile Number:
Capacity Details
Total DC Generation (kW):
Total AC Capacity (kVA):
Maximum Allowable Export (kW):
No. of Phases to Premise:
No. of Phases with DER Installed:
Islandable Installation? (Yes/No)
Is EG shared by more than one NMI? (Yes/No)
Central Protection Device | Installed settings MUST align with the embedded generation agreement | Installer Initials
Hard Export Limit (kW)
Hard Export Time Delay (s)
Underfrequency Prot Setting (Hz)
Underfrequency Prot Time Delay(s)
Overfrequency Prot Setting (Hz)
Overfrequency Prot Time Delay(s)
ROCOF Prot Setting (Hz/s)
ROCOF Prot Time Delay (s)
Vector Shift Prot Setting (deg.)
Vector Shift Prot Time Delay (s)
NVD Prot Setting (V)
NVD Prot Time Delay (s)
Undervoltage Prot Setting (V)
Undervoltage Prot Delay (s)
Overvoltage Prot Setting (V)
Overvoltage Prot Delay (s)
Sustained Overvoltage Prot Setting (V)
Sustained Overvoltage Prot Delay (s)
Reconnection Time Delay (s)
Note on A37: UE: Islanding of installation will need to be negotiated with UE and shall form part of the embededd generation agreement.
Note on A51: UE: Neutral Voltage Displacement

## Inverter Details
No. of different inverter models: | 1 | Please only fill in the blue coloured boxes
Inverter Model Count | Model #1
Inverter Model
Inverter Manufacturer
Inverter Quantity | 1
Inverter Capacity (kVA)
Total Inverter Capacity (kVA) | 0
Serial Numbers | Model #1
Inverter #1
Note on A1: UE: For example, if the site has the following inverters: 1 x Fronius SYMO 8.2-3-M 2 x Fronius ECO27.0-3-S 1 x SMA STP25000TL The no. of different inverter models is 3
Note on A4: UE: The exact model as per CEC website has to be entered. Please refer to CEC website for list of approved inverters. https://www.cleanenergycouncil.org.au/industry/products/inverters/approved-inverters
Note on A5: UE: The exact manufacturer as per CEC website has to be entered. Please refer to CEC website for list of approved inverters. https://www.cleanenergycouncil.org.au/industry/products/inverters/approved-inverters
Note on A6: UE: This is the number of inverter per model
Note on A7: UE: This is the capacity (max continuous rating) of each individual inverter of that model
Note on A10: UE: Serial numbers will need to be entered for each inverter installed

## Inverter Prot and Control
Inverter Protection Function | Inverter Protection Settings | Installer Initials
Sustained Overvoltage Prot Setting (V)
Sustained Overvoltage Prot Delay (s)
Undervoltage Prot Setting (V)
Undervoltage Prot Delay (s)
Overvoltage 1 Prot Setting (V)
Overvoltage 1 Prot Delay (s)
Overvoltage 2 Prot Setting (V)
Overvoltage 2 Prot Delay (s)
Underfrequency Prot Setting (Hz)
Underfrequency Prot Time Delay(s)
Overfrequency Prot Setting (Hz)
Overfrequency Prot Time Delay(s)
Reconnection Time Delay (s)
Soft Export Limit (kW)
Inverter Other Details | Setting | Installer Initials
Fstop-CH (Hz)
Fstop (Hz)
Inverter Volt-Watt Response | Inverter Control Settings | Installer Initials
Is this function enabled?
V1
Power output at V1 (%)
V2
Power output at V2 (%)
V3
Power output at V3 (%)
V4
Power output at V4 (%)
Inverter Volt-Var Response | Inverter Control Settings | Installer Initials
Is this function enabled?
V1
Reactive power at V1 (%)
V2
Reactive power at V2 (%)
V3
Reactive power at V3 (%)
V4
Reactive power at V4 (%)
Installer Sign Off |  | Installer Initials
I, the installer, confirm that ALL inverters on this site have been installed with the protection and control settings above
Note on A18: UE: Refer to AS4777.2:2015 Section 7.5.3.2
Note on A19: UE: Refer to AS4777.2:2015 Section 7.5.3.1
Note on A35: UE: Use + to denote leading and - to denote lagging
Note on A37: UE: Use + to denote leading and - to denote lagging
Note on A39: UE: Use + to denote leading and - to denote lagging
Note on A41: UE: Use + to denote leading and - to denote lagging

## DC Connections
No. of different DC models: | 1 | Please only fill in the blue coloured boxes
DC Model Count | DC Model #1
DC Source (Wind/Solar/Storage)
DC Model
DC Manufacturer
DC Rating (kW or kWh)
Quantity of DC Devices Connected To | DC Model #1
Inverter Model #1
Note on A1: UE: For example, if the site has the following DC models: 200 x Solar Panel Model 1 100 x Solar Panel Model 2 1 x Battery Model 1 The no. of different DC models is 3
Note on A4: UE: The exact model as per CEC website has to be entered. Please refer to CEC website for list of approved inverters. https://www.cleanenergycouncil.org.au/industry/products/inverters/approved-inverters
Note on A5: UE: The exact modules/battery model as per CEC website has to be entered. Please refer to CEC website for list of modules/batteries. https://www.cleanenergycouncil.org.au/industry/products/modules https://www.cleanenergycouncil.org.au/industry/products/batteries
Note on A6: UE: The exact modules/battery manufacturer as per CEC website has to be entered. Please refer to CEC website for list of modules/batteries. https://www.cleanenergycouncil.org.au/industry/products/modules https://www.cleanenergycouncil.org.au/industry/products/batteries
Note on A7: UE: This is the rating of ONE unit (e.g. the rating of one solar panel). If the DC Source is a battery, enter the kWh rating of the battery. If solar or wind, enter the kW rating.
Note on A9: UE: Provide the quantity of DC Model connected to each Inverter Model

## Remote Monitoring Tests
Remote Monitoring Tests
Scenarios | Notification Received by System Owner (Yes/No) |  | Installer Initials
Normal Operation
Loss of Inverter
Loss of Mains
Protection Relay Failure
Function Testing
Tests | Results | Pass/Fail | Installer Initials
Protection Trip (Example - isolate one phase voltage input to the relay) | Contactor Open or Circuit Breaker Trip
Power supply to protection relay fail (Isolate power supply to relay only) | Contactor Open
Loss of supply to protection circuit (Isolate supply to contactor coil circuit) | Contactor Open
Loss of Supply to portection circuit (Where applicable isolate supply to repeater relays) | Contactor Open

## Anti-Islanding Tests
Anti-Islanding Tests | PASS | FAIL
Inverter Number | Inverter disconnect time (must be ≤ 2 seconds) | Inverter reconnect time (must be ≥ 60 seconds) | Installer Initials
Inverter #1

## Submission Checklist
Prescribed CES | Confirmed Attached to Email
This is a statutory requirement of Energy Safe Victoria (ESV). All electrical works defined by ESV as ‘Prescribed’ (which includes generator installations) must be issued a Prescribed Certificate of Electrical Safety (CES) by the Registered Electrical Contractor (REC) upon completion of works. A copy of the CES must be provided to ESV, United Energy and the end customer and any other applicable stakeholders.
Electrical Work Request (If Required) | Confirmed Attached to Email
The Electrical Work Request (EWR) is a request form required for bi-directional metering upgrade. Until such time as the customer’s metering is upgraded, any exporting generation system may not be metered to properly compensate the end customer. The EWR form is to be provided to United Energy and the end customer.
Overall System Installation | Installer Initials
We, the installer, hereby confirm that the system has been installed in strict accordance with the Generation Agreement and all drawings and other documentation submitted to United Energy.
End Customer Notification | Installer Initials
An embedded generator customer is subject to an elevated level of responsibility (being the asset owner of an energy source which connects to and interacts with the network). The installer of the generation system is obligated to provide the end customer with all equipment operating manual/s and appropriate training such as to impart adequate knowledge of the generation system for day to day operation and any abnormal or emergency response action. The installer/proponent is required to demonstrate such action being undertaken and complete by providing UE with acknowledgement of the end customers receipt notification. We, the installer, have issued all operating manual/s to the end customer and provided appropriate training with regard to the safe operation of the generation system.
CEC Checklist Completed | Installer Initials
We, the installer, hereby confirm that the CEC Checklist has been completed and that all required signage have been installed as per AS4777.
Secondary Injection Tests | Confirmed Attached to Email
Secondary injection testing is required on each independent protection relay/s installed as part of the system. Please attach a copy of the actual test results so as to demonstrate that the performance of the independent protection relay/s is as agreed with United Energy.
Export Limit Test (where applicable) | Confirmed Attached to Email
If export limit is required as part of the embedded generation agreement, please provide evidence that the export limit on the inverters are functioning as expected.
Other Commissioning Results (where applicable) | Confirmed Attached to Email
Please provide results from any other commissioning tests that were requested as part of the technical review.